## Sheet1
Number | Type | Short description | Location | Country | End users | Heat source | Description | Cooling | Heat source-network connection | Booster HP or no for SH | Booster HP, IHEU or DHSU for DHW | TES | Centralized/ Decentralized TES | Category | Costs/Price [€] (Investment; Operation; Cost for the consumer) | Tsource [°C] | ∆Tsource [°C] | Tsupply,min [°C] (network) | Tsupply,max [°C] (network) | Tsupply,min [°C] (at consumer substation) | Tsupply,max [°C] (at consumer substation) | Treturn [°C] (network) | SCOP=(reference annual heating demand)/(seasonal electricity consumption for heating) [-] | SEER=(reference annual cooling demand)/(annual electricity consumption for cooling) [-] | Installed capacity [MW] | Produced heating energy [MWh/year] | Heating demand [MWh/year] | Building heat demand kWh/m2/year | Network length [km] (if not specified-pipes, trench specified) | Project area [km2] | Plot ratio=(building area)/(land area) | Heat loss [%] | Heat density=(delivered heat)/(covered area) [MWh/m2] | LHD (linear heat density)=(total heat demand)/(length of network) [kWh/m/year] | LHPDD (linear heating power demand density)=(installed thermal power capacity)/(network length(pipes)) [kW/m] | Reference 1 | Reference 2 | Reference 3 | Reference 4 | Reference 5
1 | NTDH | NTDH utilizing sea water for multipurpose complex heating | "Complesso della Torre” district - Savona | Italy | Multipurpose complex-Hotel****, Offices, Shops and Apartments | Sea water | Sea water runs through 3 HEXs (on the other side of HEX eater loop runs which supplies HPs); Hotel has 2 WSHPs (400 kW each); 4 air to air HPs with heat recovery system used for air exchange; Rest of the complex has 150 WSHPs used for air conditioning; Rest of the complex has centralized DHW preparation with other WSHPs | Yes | HEX | HP | HP |  |  | 1.7.1.1.1. |  | 19 | 3 | [7 empty] | 7.4 | [10 empty] | https://tbiaircon.co.uk/wp-content/uploads/2018/03/clivet_installations.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | https://seadrion.adrioninterreg.eu/wp-content/uploads/2019/02/D.T1.1.1-Report-on-heat-pump-installation-and-industry-in-Adriatic-Ionian-region-1-1.pdf | http://www.repowermap.org/installations/563587126/it/Pompa-di-calore-Savona
2 | NTDH | NTDH utilizing sea water for district heating | "Arsenale Nord” district - Venice | Italy | Area of Venice Arsenal | Sea water/Gas | Sea water is brought to central HE plant (3 HEX, one is back-up-every has capacity of 3000 kW) where it exchanges heat with water used in HPs in industrial and residential sector (for air conditioning and DHW); Gas boiler if system fails | Yes | HEX | HP | HP |  |  | 1.8.1.1.1. |  | 8 (winter) | 3 (winter) | 6 (winter) | 7 (winter) | 40 (winter) | 46 (winter) | 1.5 (network-winter); 40 (consumer-winter) | 5 |  | 6 | [10 empty] | http://tesi.cab.unipd.it/45732/1/TESI_-_ORDIGONI_GIULIO_1014607.pdf | https://doi.org/10.1016/j.rser.2018.12.059
3 | NTDH | NTDH utilizing sea water for luxury village heating | "Porto piccolo Sistiana" - Trieste | Italy | Luxury village-460 residential units, public and private beaches, parks, bars and restaurants, retail units, 5 star hotel, marina with 124 berths and a large spa area | Sea water | 18 heat pumps; Sea water used in plants over the area for heating/cooling of water (HEX); Water in main loop used by WSHPs | Yes | HEX | HP | HP |  |  | 1.7.1.1.1. | Investment: 25 mil. € | 28 (summer); 11 (winter) |  | 10 (winter) | 35 (summer) | 40 (winter) |  | 5 (winter); 30 (summer)* |  |  | 4.5 |  |  |  | 2 | [5 empty] | 2.25 | https://tbiaircon.co.uk/wp-content/uploads/2018/03/clivet_installations.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.airu.it/visita-di-airu-al-sistema-di-climatizzazione-ad-acqua-di-mare-di-portopiccolo/ | https://seadrion.adrioninterreg.eu/wp-content/uploads/2019/02/D.T1.1.1-Report-on-heat-pump-installation-and-industry-in-Adriatic-Ionian-region-1-1.pdf
4 | NTDH | NTDH utilizing ground water for district heating | Ospitaletto | Italy | Schools, gyms and multifamily houses | Ground water/Excess heat | Water from wells delivers heat to HPs at substations; Heat provided by means of waste heat from steel factory (from cooling towers) and 2 water wells; HPs to extract heat from industry | Yes | HP (excess heat); Central HP utilizes ground water?/Water through HEX exchanges heat with network?/Ground water runs through the network? (ground water-Missing info) | HP | HP |  |  | 2.2.1.1.1. |  |  |  | 13 | 25 |  |  |  | 4.14 |  | 2.5 (water HP 1.36) | 232 (recovered heat only for DHW (useful heat: 325); Missing info for SH |  |  | 2.3 | [5 empty] | 0.6 | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.mijnwater.com/wp-content/uploads/2019/08/20190729_LIFE4HeatRecovery-first-newsletter.pdf
5 | NTDH | NTDH utilizing ground water for community heating | Sale Marasino | Italy | School complex consisting of the elementary school, kindergarten, library and sports hall | Ground water | 3 heat pumps connected to 50 m deep well; Thermal power plant for historic buildings* | Yes | HEX | HP | HP | Tank TES | Centralized | 1.4.1.1.1. | Investment: 131 mil. €; To renovate thermal power plant additional: 0.98 mil. €; Savings: 0.038 mil. € |  |  | 12 |  |  |  |  | 4.25 |  | 0.14 | 195 (only part of heating needs) |  |  | 0.1 | [5 empty] | 1.4 | http://www.comunirinnovabili.it/comune-di-sale-marasino/ | https://doi.org/10.1016/j.rser.2018.12.059
6 | NTDH | NTDH utilizing ground heat for residential heating | Wüstenrot | Germany | 25 buildings in Wüstenrot suburb | Ground/Excess heat | Heat pumps in every building connected to central geothermal network (raising temperature of water heated by agrothermal source); Possible use of waste heat from chillers and waste water treatment plant | Yes | HEX (ground); HEX? (excess heat-Missing info) | HP | HP | Horizontal ground HEX (agrothermal collector); Every building has separate storage | Centralised/Decentralised | 2.4.1.1.1.* | Investment: 0.4 mil. € (network also incudes solar panels, biomass boilers and heat recovery from local food market) | 10.15 (ground) |  | 5 | 15 | 30 | 40 |  | 4.45 |  | 0.23; 2.5 (total with excess heat) |  | 450 |  | 0.5 (trench) | 0.015 |  |  |  | 900 (calculated from data-trench length) | 5 (calculated from data-trench length) | https://www.carmen-ev.de/biogene-festbrennstoffe/waermenetze/1966-waermenetze-neu-gedacht | https://doi.org/10.1016/j.rser.2018.12.059 | https://backend.orbit.dtu.dk/ws/portalfiles/portal/142226895/Untitled.pdf | https://www.mijnwater.com/wp-content/uploads/2019/08/20190729_LIFE4HeatRecovery-first-newsletter.pdf | https://www.bbr-online.de/fileadmin/bbr-daten/Hefte_2013/2013_03/bbr_0313_58_63_Pietruschka.pdf
7 | NTDH | NTDH utilizing ground water for residential heating | "Neumatten" area in March Hugstetten | Germany | 38 buildings with 151 apartments | Ground water | Heat pumps (at consumer substations) fed by water from network connected to water wells | Yes | Ground water runs through the network | HP | HP |  |  | 1.4.1.2.1. |  |  |  | 10 | 12 | [5 empty] | 0.76 |  | 1600 |  | 2.5 |  |  |  |  | 640 (calculated from data) | 0.3 | https://www.osti.gov/etdeweb/biblio/20977656 | https://www.carmen-ev.de/biogene-festbrennstoffe/waermenetze/1966-waermenetze-neu-gedacht | https://www.enbw.com/media/downloadcenter-konzern/kommplus/kommplus_2009_2-2.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.researchgate.net/publication/261011869_Die_Versorgung_eines_Neubaugebietes_mit_Kalter_Nahwarme
8 | NTDH | NTDH utilizing excess heat and ground for heating of Aurich neighbourhood | Aurich | Germany | East Frisian town and sport hall | Ground/Excess heat | Excess heat (at a temperature between 25 and 35 °C from local dairies) transfer heat at heat exchangers to water, WSHPs use that water (each 85kW), for sports hall needed temperature 55°C | Missing info | HEX | HP | HP |  |  | 2.2.1.1.1. |  | 30 (excess heat) |  | 12 | 25 |  |  |  | 4.5 |  | 1.5 |  |  |  | 2 | [5 empty] | 0.8 | https://www.dbu.de/phpTemplates/publikationen/pdf/0709100210358pps.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.klimaschutz-niedersachsen.de/_Resources/Persistent/200806d97e7a0db094a4e922c872d4491f45bd81/2018-02-15_04_Ubben-Aurich.pdf
9 | NTDH | NTDH utilizing solar collectors and ground for residential buildings heating | "Sohnius-Weide" district in Nümbrecht | Germany | 13 residential buildings | Ground/Solar | Traditional solar thermal flat plate collectors and ground network with brine water which feeds HEX; Other side of HEX connected with HPs at consumer substations for SH and DHW; Plans to connect to sewer treatment plant in future | Missing info | HEX | HP | HP | Horizontal ground HEX; Rainwater tank | Centralized | 1.2.1.1.1. | Investment: 0.32 mil. € |  |  | 4 | 21 |  |  |  | 4.23 |  | 6, 8, 11 and 18 kW (HPs) |  |  |  | 1.2 | [6 empty] | https://www.energieagentur.nrw/eanrw/kaltes_nahwaermenetz | https://www.sonnewindwaerme.de/solarthermie-waermepumpe/kaltes-nahwaermenetz-versorgt-neubaugebiet | https://installation-dkz.de/wp-content/uploads/2017/09/26-28_web.pdf | https://doi.org/10.1016/j.rser.2018.12.059
10 | NTDH | NTDH utilizing ground heat for residential heating | "Hochvogelstraße" area in Biberach | Germany | 45 low-energy houses | Ground | Heat pumps (using water-glycol mixture from network, heated by ground)) installed at consumer substation for SH and DHW; For higher temperatures heat pumps can be equipped with additional heat element; Primary loop connected to secondary loop through 2 HPs, secondary loop leads to consumers; possibility of installation IHEU at HP for higher temperatures | Yes | HP | HP | HP | Vertical ground HEX (34 boreholes 200 m depth) | Centralized | 1.1.1.2.1. | Investment: 2 mil. € (mostly for explorations and drilling) | 12 |  | 0 | 20 |  | 35 | [7 empty] | 2.44 | [6 empty] | https://www.energiezukunft.eu/erneuerbare-energien/waerme/geothermie-kalte-nahwaerme-in-biberach/ | https://www.ewa-riss.de/de/Waerme/Waermeversorgung-in-Biberach/Waermeversorgung-in-Biberach.html | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.wiesbadener-kurier.de/lokales/wiesbaden/nachrichten-wiesbaden/neue-technik-soll-geplante-hauser-am-biebricher-schlosspark-beheizen_18449052
11 | NTDH | NTDH utilizing ground and excess heat for residential heating | "Stiegelpotte" area in Spenge | Germany | 110 residential buildings with 130 residential units | Ground/Excess heat | Excess heat (industrial excess heat from compressors used to compress air from traditional weaving mill (fossils)) transferred via HE to brine water which feeds heat pumps in each building (up to 40 kW) | Missing info | HEX | HP (per residential complex) | HP (per residential complex) |  |  | 2.2.1.1.1. | Investment: 1.33 mil. € | 20 (excess heat) |  |  |  | 30 | 55 | 15 | 4.3 |  | 0.7 |  |  |  |  | 0.08 | [5 empty] | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.diekaelte.de/sites/default/files/ulmer/file_172029.pdf | http://www.klima-log.de/projekt.asp?InfoID=6800
12 | NTDH | NTDH utilizing excess heat for residential park heating | "Sattlerweg" area in Herford | Germany | Residential park (240 residential units) | Excess heat | Excess heat (process excess heat at a temperature between 25°C and 35°C from local dairies) heats brine water in HEX; 16 decentralized heat pumps per residential complex which use that brine water for SH and DHW | Missing info | HEX | HP | HP |  |  | 2.1.1.1.1. | Price for consumers (without tax): heat-base part (162.00 €/year), variable part (9.00 ct/kWh); DHW- for heating- base part (57.00 €/year), variable part (8.37 €/m3); DHW-portable water- base part (57 €/year), variable part (10.12 €/m3) | 30 |  |  | 23 | 35 | 50 |  | 4.6 |  | 15 to 105 kW (16 larger HPs per residential complex) |  |  |  | 0.7 | [6 empty] | https://doi.org/10.1016/j.rser.2018.12.059 | https://energieservice-ww.com/wohnpark-sattlerweg-privat.html | https://www.diekaelte.de/sites/default/files/ulmer/file_172029.pdf
13 | NTDH | NTDH utilizing air and ground for heating houses | "Obstanger" area in Herford | Germany | 70 detached houses (at the end of the project 200) | Ground/Air | Dry cooler (100 kW) and 2 heat pump (each 240 kW) are a central source which preheats brine-water mixture; in every building heat pump to raise temperature | Missing info | HP (ground and air) | HP | HP | Vertical ground HEX (19 boreholes 100 m depth) | Centralized | 1.3.1.2.1. |  |  |  | 10 | 15 | 35 | 55 |  | 4.7 |  | 0.58 (+ each building can install HPs 5 to 20 kW to raise temperature) | [10 empty] | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.diekaelte.de/sites/default/files/ulmer/file_172029.pdf
14 | NTDH | NTDH utilizing ground heat for residential heating | "Karl-May-Weg" district in Fischerbach | Germany | 26 buildings | Ground | Network in ground in which brine water flows (ground heats or cool brine water); Brine water used at consumer HP for SH and DHW | Yes | HEX? (Missing info) | HP | HP | ICE storage (320 m3) | Centralized | 1.1.1.1.1.* | Investment: 1.1 mil. € |  |  | 0 | 25 | 35 |  |  | 4.7 |  | 0.185 |  |  |  | 1 | [5 empty] | 0.2 | https://www.buerger-energie-fischerbach.de/de/bKWN/Karl-May-Weg-II%2BIII | https://www.e-werk-mittelbaden.de/projekt/bidirektionales-kalt-waerme-netz-bkwn | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.badenova.de/mediapool/media/dokumente/unternehmensbereiche_1/stab_1/innovationsfonds/abschlussberichte/2013_13/2013-14_Abschlussbericht_KWnetz_Fischerbach.pdf
15 | NTDH | NTDH utilizing ground for house heating | "Max-Ernst-Straße" area in Schifferstadt | Germany | 38 houses | Ground | Brine circulates through network and goes to central station from which it goes to HP (at consumer substations) for SH and DHW | Yes | HEX? (Missing info) | HP | HP | Vertical ground HEX (28 boreholes 100 m depth) | Centralized | 1.1.1.1.1.* |  | 12 | [8 empty] | 0.23 | [10 empty] | https://www.energieagentur.rlp.de/service-info/die-energieagentur-informiert/aktuelle-meldungen/aktuelles-detail/kalte-nahwaerme-konzept-der-energieagentur-ueberzeugt-schifferstadt/ | https://doi.org/10.1016/j.rser.2018.12.059
16 | NTDH | NTDH utilizing ground heat for residential area heating | "Küferweg" district in Mainz | Germany | Residential area | Ground | Ground used to heat brine water mixture and then that brine water is used for SH and DHW at substations (14 HPs); HEX between network and substation | Missing info | HEX? (Missing info) | HP | HP | Vertical ground HEX (4 boreholes 300 m depth); In every house storage | Centralized/Decentralized | 1.1.1.1.1.* |  |  |  | 8 | 9 |  |  |  | 3.85 |  | 0.112 | [10 empty] | https://gemuenden-bau.de/geothermie-nahwaermeversorgung-im-einfamilienhaus/ | https://www.mainz.de/microsite/klimafit/medien/bindata/Klimaschutzbericht_Mainz_2013.pdf | https://www.mainz.de/microsite/klimafit/medien/bindata/MPK_Mainz_Endbericht.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.tsb-energie.de/fileadmin/Redakteure/Veranstaltungen/Gebaeudeenergie/2017/Vortraege/Hr._Prof._Giel__TSB.pdf
17 | NTDH | NTDH utilizing river heat and solar for house heating | Ohrberg | Germany | 69 planned single-family houses (low energy) | River/Solar | 2 central HPs (185 kW each) for preheating brine water which goes to HPs at consumer substation for SH and DHW (5 to 20 kW); Solar thermal used for DHW | Missing info | HP (river); Solar collectors | HP | HP and solar collectors | Tank TES (400 l) | Centralised | 1.11.1.1.1. |  | 3.7 |  | 10 | 12 | 45 | 55 | 6; 35 (consumer) |  |  | 0.37 (each house has its own heat pump outputs from 5 to 20 kW) |  |  |  |  | 0.08 | [5 empty] | https://wpuq.de/solarsiedlung/ | https://www.fvee.de/fileadmin/publikationen/Themenhefte/th1997/th1997_02_03.pdf | https://www.diekaelte.de/sites/default/files/ulmer/file_172029.pdf | https://doi.org/10.1016/j.rser.2018.12.059
18 | NTDH | NTDH utilizing ground water for heating houses | Troisdorf | Germany | Approx. 100 houses | Ground water | Use of ground water that runs through network; Water feeds HPs at consumer substations | Missing info | Ground water runs through the network | HP | HP |  |  | 1.4.1.2.1. |  |  |  | 10 | 10 | [9 empty] | 5 | [6 empty] | https://www.stadtwerke-troisdorf.de/fileadmin/user_upload/5.0_Service/Download-center/Geothermie/Bescheinigung_Primaerenergiefaktor_Eschmar_West.pdf | http://www.troisdorf.de/web/de/stadt_rathaus/aktuelles/presse/pressemitteilungen.htm?Selection=095&jahr=2014 | http://geothermie-schweiz.ch/wp_live/wp-content/uploads/2016/01/04_Sanner_EGEC_GeoDH_Projekt_und_Smart_Thermal_Grids.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.energate-messenger.de/news/186857/stadtwerke-troisdorf-setzen-auf-kalte-nahwaerme
19 | NTDH | NTDH utilizing ground water for heating buildings | Dorsten-Wulfen | Germany | 71 buildings | Ground water | Heat pumps in every building (fed by ground water from main network*) | Missing info | Central HP utilizes ground water?/Water through HEX exchanges heat with network?/Ground water runs through the network? (Missing info) | HP | HP |  |  | 1.4.1.1.1.* |  |  |  | 10 | 10 | [5 empty] | 1.1 |  |  |  | 1.2 | [5 empty] | 0.9 | http://www.dorsten.de/Verwaltung/Presse/Aktuelle_Meldungen/Waermekonzept.pdf | https://doi.org/10.1016/j.rser.2018.12.059
20 | NTDH | NTDH utilizing excess heat and ground heat for residential heating | "Berender Redder" area in Schleswig | Germany | 250 residential units | Ground/Excess heat | Excess heat and ground heat brine water* that is delivered to HPs at substations for SH and DHW | Yes | HEX? (ground and excess heat-Missing info) | HP | HP |  |  | 2.2.1.1.1.* | At link (Reference 1) all prices are shown, heat price 7.084 Ct/kWh; Substation cost: 7799 € |  |  | 12 | 12 |  |  |  | 4.5 |  | 0.572 |  |  |  | 10 | [5 empty] | 0.1 | https://www.schleswiger-stadtwerke.de/content/produkte/schleswigerNAHWAERME/ | https://doi.org/10.1016/j.rser.2018.12.059
21 | NTDH | NTDH utilizing ground heat for campus heating | ETH Campus Hönggerberg in Zürich | Switzerland | University campus | Ground/Excess heat | Heat is extracted from ground to fluid. then it is transported to cluster HPs for SH, DHW is prepared with HEX; Excess heat from cooling | Yes | HEX? (ground and excess heat-Missing info) | HP (per cluster) | electric boiler (per building) | 3 Vertical ground HEXs (431 boreholes 200 m depth) | Centralized | 2.4.1.1.2.* | Investment: 35 mil. € | 16 (ground) |  | 8 | 24 | 30 | 35 | 12 | 5.8 | 6.9 | 5.5 |  | 28450 |  | 1.5 | 0.475 |  |  |  | 18966.667 (calculated from data) | 3.7 | https://pubdb.bfe.admin.ch/de/publication/download/8836 | https://ethz.ch/content/dam/ethz/main/eth-zurich/nachhaltigkeit/infomaterial/Anergienetz_A4_6s_Einzel_RZ.pdf | https://doi.org/10.1016/j.rser.2018.12.059
22 | NTDH | NTDH utilizing ground water for residential heating | Jardins de la Pâla, Bulle | Switzerland | 81 apartments | Ground water | Heat is transferred through HE to network; Network supplies HPs for SH and DHW | Yes | HEX | HP | HP |  |  | 1.4.1.1.1. | Investment: 3.798 mil. €; Variable heat price 4 ct./kWh and DHW 7 ct./kWh | 10.5 |  | 8 | 9 | 35 | 45 | 4 | 2.7 | 12 | 2 |  | 2100 |  | 0.85 | 0.065 |  |  |  | 2470.588 (calculated from data) | 2.4 | https://pubdb.bfe.admin.ch/de/publication/download/8836 | https://doi.org/10.1016/j.rser.2018.12.059 | https://heatpumpingtechnologies.org/annex47/wp-content/uploads/sites/54/2018/12/annex-47sub-projetcsbulle.pdf
23 | NTDH | NDH utilizing excess heat for residential heating | Familienheimgenossenschaft district in Zürich (FGZ) | Switzerland | 25 settlements | Ground/Excess heat | Excess heat (data centres and chillers) used to heat network, in summer heat is stored in ground for use in winter; network connected to HPs at substations for SH and DHW | Yes | HEX? (ground and excess heat-Missing info) | HP | HP | 2 Vertical ground HEXs (332 boreholes 250 m depth) | Centralised | 2.4.1.1.1.* | Investment: 40.383 mil. €; Variable heat price 17 ct./kWh |  |  | 8 | 28 | <30 (new buildings) | >70 (existing buildings) | 14 | 4.1 |  | 3.93 | 80000 (excess heat) | 27000 |  | 1.5 |  |  | 33.75 (calculated from data) |  | 18000 (calculated from data) | 2.6 | https://pubdb.bfe.admin.ch/de/publication/download/8836 | https://pdfs.semanticscholar.org/c5c5/383cc0ae6b8eff492b4662bcb022bc11e344.pdf | https://doi.org/10.1016/j.egypro.2017.07.443 | https://www.velasolaris.com/wp-content/uploads/2018/12/konferenzbuch-siges2016.pdf
24 | NTDH | NTDH utilizing excess heat and PTV for heating | Suurstoffi district-Risch Rotkreuz | Switzerland | Office complex, residential objects, schools, administrative and sports buildings | Ground/Excess heat/Solar | Excess heat from free cooling and heat from solar collectors regenerate soil (seasonal storage) which then heats network connected to HPs at substations for SH and DHW; Solar energy is also used directly for SH and DHW | Yes | HEX? (ground and excess heat Missing info); Solar collectors | HP (for few buildings) | HP (for few buildings) | Vertical ground HEX (215 boreholes 150 m depth and 180 boreholes 280 m depth) | Centralized | 2.4.1.1.1.* |  |  |  | 8 | 25 | 35 |  | 10.5 | 3.8 | 12.1 | 5.431 |  | 7653 |  | 2.5 | 0.17 |  |  |  | 3061.2 (calculated from data) | 2.172 (calculated from data) | https://pubdb.bfe.admin.ch/de/publication/download/8836 | doi.org/10.1016/j.energy.2017.03.137 | https://infoscience.epfl.ch/record/213373 | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.novatlantis.ch/wp-content/uploads/2015/01/20140821_Poster_Monitoring_print.pdf
25 | NTDH | NTDH utilizing lake water for heating buildings | La Tour-de-Peilz | Switzerland | Around 300 buildings (mostly residential) | Lake water | Lake water transfer heat to distribution network through HE; Distribution network is connect to substations with HPs (10 kW to 500 kW) for SH and DHW | Yes | HEX | HP | HP |  |  | 1.5.1.1.1. | Investment: 30 mil. € | 7 | 4 | 2 | 20 | 55 | 60 | 9 | 3.75 |  | 10 |  | 18.5 |  | 4.1 |  |  |  |  | 4.512 (calculated from data) | 2.4 | https://pubdb.bfe.admin.ch/de/publication/download/8836 | https://doi.org/10.1016/j.rser.2018.12.059
26 | NTDH | NTDH utilizing ground water for residential heating | "Krommen Kelchbach" district in Natres | Switzerland | 12 buildings (180 residential units) | Ground water | Ground water transfers heat (to network or directly*) to HPs at substations for SH and DHW | Missing info | Central HP utilizes ground water?/Water through HEX exchanges heat with network?/Ground water runs through the network? (Missing info) | HP | HP |  |  | 1.4.1.1.1.* |  |  |  | 8 | 18 | [7 empty] | 1800 | [8 empty] | https://www.brig-glis.ch/online-dienste/stadtinfo/files27/info37energie_brig_screen.pdf | https://www.enalpin.com/newsletter/files36/newsletter-nr.1-2016.pdf | https://doi.org/10.1016/j.rser.2018.12.059
27 | NTDH | NTDH utilizing ground water for residential heating | Brig-Glis | Switzerland | 5 buildings (50 apartments) | Ground water | Ground (ground water) heats network which is connected to 5 HPs at consumer substations for SH and DHW | Yes | Central HP utilizes ground water?/Water through HEX exchanges heat with network?/Ground water runs through the network? (Missing info) | HP | HP |  |  | 1.4.1.1.1.* |  |  |  | 8 | 18 |  |  |  | 4 |  |  |  | 410 | [8 empty] | https://www.brig-glis.ch/online-dienste/stadtinfo/files27/info37energie_brig_screen.pdf | https://www.enalpin.com/newsletter/files36/newsletter-nr.1-2016.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.brig-glis.ch/energiestadt/files12/flyer_masterplanenergie18_online.pdf
28 | NTDH | NTDH utilizing ground water for heating apartments, hotel etc. | Oberwald/Obergoms | Switzerland | 209 apartments, 1 hotel and other public buildings | Ground water | Exploits a Geostructure (the “Furkatunnel”) as a thermal source at 16 °C through which runs hot water which is distributed to HPs at substations for SH and DHW | Missing info | Ground water runs through the network | HP | HP |  |  | 1.4.1.2.1. | Investment: 1.31 mil. € | 15.5 |  | 15 | 16 | [5 empty] | 1.337 |  |  |  | 2.2 | [5 empty] | 0.6 | https://www.enalpin.com/newsletter/files36/newsletter-nr.1-2016.pdf | http://www.energieregiongoms.ch/index.php/projekte/item/20-warmwasser-aus-dem-furkatunnel | https://www.anog.ch/news/infoveranstaltungen/informationsveranstaltunganog.pdf | https://pangea.stanford.edu/ERE/db/WGC/papers/WGC/2015/01062.pdf | https://doi.org/10.1016/j.rser.2018.12.059
29 | NTDH | NTDH utilizing excess heat for community heating | "Visp-West" district - Visp | Switzerland | Community Visp | Excess heat | Excess heat from a chemical process with a temperature range between 8 and 18 °C used for heating network fluid which delivers heat to consumer substation HPs for SH and DHW | Yes | HEX | HP | HP |  |  | 2.1.1.1.1. | Investment: 1.774 mil. € | 13 |  | 8 | 18 | 30 | 55 | 10 | 4 |  | 1.624 |  | 5825 (SH) 2912 (DHW) |  | 4.2 | 0.16 |  |  |  | 2080.238 (calculated from data) | 0.4 | https://pubdb.bfe.admin.ch/de/publication/download/8836 | https://www.visp.ch/onlineschalter/formulare/formularegemeinde/files10/anergienetz.pdf | https://www.1815.ch/rhonezeitung/zeitung/region/visper-anergienetz-frostige-stimmung-bei-den-anwohnern/ | https://doi.org/10.1016/j.rser.2018.12.059 | https://books.google.de/books?id=75eBDwAAQBAJ&pg=PA168&lpg=PA168&dq=anergienetz+geneve+lac+nations&source=bl&ots=_nAf-Sr5jH&sig=ACfU3U353AezV3S-o-qwYc8oh-zIFeYatA&hl=de&sa=X&ved=2ahUKEwi92sONkZPhAhXDI1AKHRVqAi0Q6AEwA3oECAkQAQ#v=onepage&q=anergienetz%20geneve%20lac%20nations&f=false
30 | NTDH | NTDH utilizing lake water for administrative buildings heating | Genève-Lac-Nations | Switzerland | Mainly administrative buildings (International organizations), schools and collective housing | Lake water/Gas | Pumping station pumps lake water (treated) to costumer substation for free cooling or heating by HPs | Yes | Lake water runs through the network | HP | HP | The network is used as buffer storage in winter when the network operates in a closed loop | Centralized | 1.6.1.1.1. | Investment: 30.9 mil. € | 11 | 2.5 | 5 | 17 | 40 | 45 | 8.5 | 2.5 | 8.8 | 2.9 |  | 5000 |  | 6 | 0.84 |  |  |  | 833.333 (calculated from data) | 0.5 | https://pubdb.bfe.admin.ch/de/publication/download/8836 | https://thermdis.eawag.ch/static/templates/files/ThermischeNetze_EtudeDeCas_ReseauThermiqueGeneveLacNations.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | https://books.google.de/books?id=75eBDwAAQBAJ&pg=PA168&lpg=PA168&dq=anergienetz+geneve+lac+nations&source=bl&ots=_nAf-Sr5jH&sig=ACfU3U353AezV3S-o-qwYc8oh-zIFeYatA&hl=de&sa=X&ved=2ahUKEwi92sONkZPhAhXDI1AKHRVqAi0Q6AEwA3oECAkQAQ#v=onepage&q=anergienetz%20geneve%20lac%20nations&f=false
31 | NTDH | NTDH utilizing excess heat, solar heat and ground for village heating | REKA village, Blatten-Belalp | Switzerland | Village | Ground/Solar | Solar collectors produce heat that can be directly used or can be stored in seasonal ground storage; HPs for SH and DHW; High and low temperature loop (high one needs more HPs and more solar heat); Possibility of connecting to Excess heat source | Missing info | HP (ground); Solar collectors | HP | HP | Vertical ground HEX (31 boreholes 150 m depth) | Centralised | 1.2.1.2.1. |  |  |  | 4.5 | 8 | 35 |  |  | 4.24 |  | 1 HP 70 kW and 3 HPs 72 kW | [10 empty] | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.researchgate.net/publication/265470872_Ferien_auf_der_SonnenENERGIEseite_-_REKA_Feriendorf_Blatten-Belalp
32 | NTDH | NTDH utilizing solar and ground for municipal buildings heating | "Sedrun" district in Tujetsch | Switzerland | Municipal buildings in the core zone of Sedrun | Ground/Solar | Ground probes and solar collectors connected to central stations with HEX; Fluid is distributed to consumer substation HPs for SH and DHW | Yes | HEX (ground); Solar collectors | HP | HP | Vertical ground HEX (73 boreholes 250 m depth) | Centralized | 1.2.1.1.1. |  |  |  | 8 |  |  |  | 4 | [13 empty] | http://www.energia-alpina.ch/fileadmin/user_upload/Docs/0_Reglement_2017.02.08.pdf | http://www.energia-alpina.ch/fileadmin/user_upload/Docs/4_Preisblatt_2016.pdf | http://www.energia-alpina.ch/home/ | https://doi.org/10.1016/j.rser.2018.12.059 | http://www.energia-alpina.ch/fileadmin/user_upload/Docs/Infotafel_Anergienetz_Zentrale_120x90cm.pdf
33 | NTDH | NTDH utilizing air, solar energy and ground for hostel heating | Saas Fee | Switzerland | Aqua Allalin Youth Hostel | Ground/Air/Solar | Air HPs, solar collectors and ground storage heat is transferred to central HP which heats fluid for consumer substation HPs for SH and DHW | Yes | HP (ground and air); Solar collectors | HP | HP | Vertical ground HEX (90 boreholes 150 m depth); Tank TES | Centralized | 1.3.1.1.1. |  | 10 (ground) |  | 8 | 20 |  |  | 10 |  |  | 0.56 | [10 empty] | https://www.enalpin.com/newsletter/files36/newsletter-nr.1-2016.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | https://docplayer.org/58742169-Energieapero-2016-i-ein-beitrag-zur-energiewende-enalpin-setzt-mit-dem-waermenetz-saas-fee-auf-die-erneuerbare-zukunft.html
34 | NTDH | NTDH utilizing ground water for residential complex and office building heating | "Rheinfels/Kleinbruggen" district in Chur | Switzerland | Residential complex Rheinfels III and Mazzeoleni, cantonal road traffic office building and new data center | Ground water | Ground water exchanges heat through HEX to secondary loop that feeds booster HPs at consumer substation for SH and DHW | Yes | HEX | HP | HP |  |  | 1.4.1.1.1. |  |  |  | 6 | 16 |  | 40 | 7 |  |  | 2.5 |  |  |  | 0.48 | [5 empty] | 5.2 | https://ibc-chur.ch/wp-content/uploads/2016/04/1461306229-020e5b03283499960a766d1acbe739cd.pdf | https://ibc-chur.ch/wp-content/uploads/2017/11/1511418335-7d8d4b32a23e21073c65f81c1244b6cf.pdf | https://ibc-chur.ch/wp-content/uploads/2016/04/1461226333-9cc85cef27b2f7834377c11bbfc3af37.pdf | https://doi.org/10.1016/j.rser.2018.12.059
35 | NTDH | NTDH utilizing ground heat and excess heat for heating railway station and shopping mall | Richti Wallisellen | Switzerland | Railway station, shopping mall Glatt (housing and commercial services), total area of 72.000 m2 | Ground/Excess heat | Excess heat from one part of area is transferred to network; If there is need for heating in some other area, that heat is used by substation HPs for SH and DHW; If heat is not needed heat is stored in the ground; Excess heat from cooling | Yes | HEX? (ground and excess heat-Missing info) | HP | HP | Vertical ground HEX (220 boreholes 225 m depth) | Centralised | 2.4.1.1.1.* |  |  |  | 8 | 22 |  |  | 14.5 | [7 empty] | 0.072 | [5 empty] | http://www.richti.ch/downloads/Energiekonzept-Richti-Wallisellen.pdf | https://doi.org/10.1016/j.rser.2018.12.059 | http://www.allreal.ch/nc/en/media/media-releases-ad-hoc-publicity/details/24ee3a0c86373ec3aaa79ecea8927caf/?tx_news_pi1%5Bnews%5D=475&tx_news_pi1%5Bcontroller%5D=News&tx_news_pi1%5Baction%5D=detail
36 | NTDH | NTDH utilizing sea water for heating newly built homes | Duindorp -The Hague | Netherlands | 789 new-build homes | Sea water | Depending on the water temperature sea water goes through central heat exchanger or HP; Then brine water mixture is distributed to consumer substation HPs for SH and DHW (in winter central HP raises sea water temperature, in summer only HEX) | Missing info | HP; HEX (in summer) | HP | HP |  |  | 1.7.1.1.1./1.7.1.2.1. |  | 9.5 |  | 11 | 18 | 45 |  |  | 3 |  | 1.2 | [10 empty] | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.technischweekblad.nl/nieuws/zeewater-verwarmt-huizen-in-duindorp | https://www.gshp.org.uk/pdf/DECC_Heat_Pumps_in_District_Heating_Case_studies.pdf
37 | NTDH | NTDH utilizing excess/ground heat for office space and multipurpose complex heating | Herleen | Netherlands | Office of the Central Bureau of Statistics and the complex Heerlerheide Centrum (homes, supermarket, offices, community facilities, catering), Arcus College, pension fund that owns a data center | Ground/Excess heat | Excess heat/Ground (two abandoned coal mines have been exploited as a low-temperature resource); Water from coal mines goes to central station (HEX); The second loop represents loop with booster HPs at consumer substation for SH and DHW | Yes | HEX | HP | HP | Mine water reservoir | Centralized | 2.5.1.1.1. |  | 28 | 16 | 18 | 25 | 30 |  | 17.5 | [6 empty] | 7 (3-pipe network) | [6 empty] | https://doi.org/10.1016/j.egypro.2014.01.158 | https://doi.org/10.1016/j.rser.2018.12.059
38 | NTDH | NTDH utilizing river and ground heat for heating buildings | Janseniushof project - Leuven | Belgium | Existing buildings and a new buildings | Ground/River | Heat is extracted from river and ground; River loop has HEX to transfer heat to primary loop (ground is directly connected); houses has HPs or HEX depending on their heat demand | Yes | HEX | HP | HP | Aquifer TES | Centralized | 1.2.1.1.1. |  | 20 (river) |  |  | 14 | 40 |  | 8 |  |  | 0.6 (different building has different size HPs) |  |  | 25 (new buildings) and 70 (old buildings) |  | 0.025 | [5 empty] | https://doi.org/10.1016/j.rser.2018.12.059 | http://etkhpcorder.extweb.sp.se/ViewDocument.aspx?RapportId=1808
39 | NTDH | NTDH utilizing ground heat for residential heating | Brooke Street - Derby | England | 18 apartments | Ground | 3 HPs connected with network that goes through ground storage; Each HP has 100 litre storage and is used for SH and DHW | Missing info | HEX? (Missing info) | HP | HP | Vertical ground HEX (28 boreholes 100 m depth) | Centralised | 1.1.1.1.1.* |  | 8 |  |  |  | 55 | 60 |  | 3.2 |  | 0.12 | [10 empty] | https://doi.org/10.1016/j.rser.2018.12.059 | https://www.gshp.org.uk/pdf/DECC_Heat_Pumps_in_District_Heating_Case_studies.pdf
40 | NTDH | NTDH utilizing sea water heat for campus heating | University of Bergen | Norway | University campus | Sea water | Central HP extracts heat from sea water; That heat is transferred to booster HPs at consumer substation for SH and DHW | Yes | HP | HP | HP |  |  | 1.7.1.2.1. |  |  |  | 6 | 12 | [5 empty] | 4 | [10 empty] | https://www.osti.gov/etdeweb/biblio/107886 | https://doi.org/10.1016/j.rser.2018.12.059 | http://archiwum.mos.gov.pl/g2/big/2014_10/92814fca36684fe6e89ebbe209a1fa27.pdf
41 | LTDH | LTDH Houses connected to existing DH with low temperature heating usage | Lystrup | Denmark | 40 terraced low energy houses | Existing DH | Connected to existing DH, supply water of MTDH is mixed with return water of LTDH n order to achieve low supply temperatures of LTDH | Missing info | Shunt (MTDH supply mixed with LTDH return) | No | IHEU (24.3 kW) or DHSU (4.7 kW) (Slightly lower return temperatures for IHEU) | Tank TES (120 l) | Decentralized | 3.1.2.1.1./3.1.2.1.2. | Reference 3 provide detail expenses of every aspect of this DH network-total investment 346900 €; Distribution investment cost: 115 €/m; Annual distribution cost 8.9 €/GJ | 70 |  | 52.1 | 52.7 |  | 50 | 33.9 |  |  | 0.0323 | 287211 | 232070 | 53.333 | 0.723; 0.767 (trench) | 0.017 | 0.24 | 17 | 0.013 | 277.778 | 0.04 | https://www.danskfjernvarme.dk/-/media/danskfjernvarme/gronenergi/projekter/eudp-lavtemperatur-fjv/guidelines-for-LTDH inal_rev1.pdf | http://celsiuscity.eu/wp-content/uploads/2019/11/Aarhus-Lystrup.pdf | https://www.iea-dhc.org/fileadmin/documents/Annex_X/IEA_Annex_X_Final_Report_2014_-_Toward_4th_Generation_District_Heating.pdf | https://doi.org/10.1016/j.egypro.2017.05.052
42 | LTDH | LTDH Houses connected to existing DH with low temperature heating usage | Sønderby | Denmark | 75 existing detached houses with under-floor heating | Existing DH | Connected to existing DH, 3-pipe connection shunt-return water from main network as supply of LTDH but supply water from main network can be mixed to achieve higher temperatures); Substation connected to the main network via HEX (indirect connection) | Missing info | Shunt (3-pipe connection) | No | IHEU (32.3 kW) |  |  | 3.1.2.2.1. |  | 80 |  | 55 | 55.1 | 53 | 53.2 | 40.2 (network); 37.9 (consumer substation) |  |  | 0.1454 | 1602.8 | 1383.45 | 93.68 | 2743 (trench) |  |  | 13.8 | 0.123 (calculated from data) | 504.356 (calculated from data-trench length) | 0.053 (calculated from data-trench length) | https://www.danskfjernvarme.dk/-/media/danskfjernvarme/gronenergi/projekter/eudp-lavtemperatur-fjv/guidelines-for-LTDH inal_rev1.pdf | http://celsiuscity.eu/wp-content/uploads/2019/11/H%C3%B8je-Taastrup.pdf | https://www.imp.gda.pl/ee_cities/prezentacje/drugi_C/1_Britta_Schmigotzki.pdf | https://backend.orbit.dtu.dk/ws/portalfiles/portal/142226895/Untitled.pdf
43 | LTDH | LTDH Houses connected to existing DH with low temperature heating usage | Tilst | Denmark | 8 existing detached houses with radiators | Existing DH | Connected to existing DH, shunt at the beginning of the street to reduce supply temperature-mix of return water from LTDH and MTDH supply; Two ways of connecting main network with substation: direct and indirect (with HEX) | Missing info | Shunt | No | IHEU |  |  | 3.1.2.1.1. |  | 75 |  | 61 | 66 | 55 (indirect connection) | 60 (direct connection) | Direct connection return 30; Indirect connection return 30 (primary side) and 25 (secondary side) | [6 empty] | 0.23 (trench) |  |  | 17.5 |  |  |  | https://www.danskfjernvarme.dk/-/media/danskfjernvarme/gronenergi/projekter/eudp-lavtemperatur-fjv/guidelines-for-LTDH inal_rev1.pdf | http://celsiuscity.eu/wp-content/uploads/2019/11/Aarhus-Tilst.pdf
44 | LTDH | LTDH utilizing ground heat pump for passive houses heating | Østre Hageby, Stavanger | Norway | Passive house project with 66 dwellings, consisting of both apartment blocks and terraced houses | Ground | Ground HP that feeds network | Missing info | HP | No | IHEU | Vertical ground HEX (boreholes 200 m depth) | Centralized | 1.1.2.1.1. |  |  |  | 50 | 55 |  |  | 32.5 | [13 empty] | https://www.danskfjernvarme.dk/-/media/danskfjernvarme/gronenergi/projekter/eudp-lavtemperatur-fjv/guidelines-for-LTDH inal_rev1.pdf | http://celsiuscity.eu/wp-content/uploads/2019/11/Stavanger-%C3%98stre-Hageby.pdf
45 | ULTDH | ULTDH connected to existing DH and solar collectors to heat social houses | Albertslund South | Denmark | 550 two-story row houses from the 1960's have been thoroughly refurbished into low energy houses. 1.000 courtyard houses are being totally refurbished into low energy houses. Around half way through the process. So above 1.000 houses are supplied with LTDH oday, rising to 1.550 houses within three years. They are all one family houses - owned by non-profit social housing companies. Houses are renovated to low-energy standard | Existing DH | Existing DH (biomass CHP and waste incineration); Solar collectors used also as heat source in houses; Direct connection DH to SH (floor heating) | Missing info | Shunt? (Missing info) | No | HP |  |  | 3.1.1.1.1.* |  |  |  | 35 | 40 | 35 | 40 | 12.5 (network); 20 (return from SH) | [13 empty] | https://www.danskfjernvarme.dk/-/media/danskfjernvarme/gronenergi/projekter/eudp-lavtemperatur-fjv/guidelines-for-LTDH inal_rev1.pdf | http://celsiuscity.eu/wp-content/uploads/2019/11/Albertslund.pdf
46 | LTDH | LTDH utilizing existing DH for passive house heating | Venning, Kortrijk | Belgium | A passive house area of 64 single-family houses and four multi-family houses (82 dwellings in total) | Existing DH | Existing DH (supplied by woodchip boiler) heats LTDH network | Missing info | Shunt? (Missing info) | No | IHEU | Tank TES | Centralized | 3.1.2.1.1.* |  |  |  | 50 |  |  |  | 25 |  |  | 1 (Wood chip boiler suppling main network) | [10 empty] | https://www.danskfjernvarme.dk/-/media/danskfjernvarme/gronenergi/projekter/eudp-lavtemperatur-fjv/guidelines-for-LTDH inal_rev1.pdf | http://celsiuscity.eu/wp-content/uploads/2019/11/Kortrijk-Venning.pdf
47 | LTDH | LTDH utilizing biomass boiler, ground and air heat pumps and solar collectors for house heating | Greenwatt Way, Slough | England | 10 dwellings and information center | Ground/Air/Solar | Biomass boiler, ground and air HPs and solar collectors used as a heat source of network. Main network directly connected with SH | Missing info | HP? (ground and air-Missing info); Solar collectors | No | IHEU | Tank TES 8000 l | Centralized | 1.3.2.1.1.* | Distribution investment cost: 133 €/m; Annual distribution cost 13.7 €/GJ |  |  | 50.5 | 51.7 | 50.5 | 51.7 | 34.9 (network); 35 consumer substation) | air HP 2.1; ground HP 2.9 |  | 2x17 kW (ground HP); 2x20 kW (air HP); 30 kW (biomass boiler) | 49.444 | 35.7 | 42.222 | 0.165 (trench) | 0.0018 | 0.47 | 28 | 0.019 | 222.222 | 0.6303 (calculated from data-trench length) | https://www.danskfjernvarme.dk/-/media/danskfjernvarme/gronenergi/projekter/eudp-lavtemperatur-fjv/guidelines-for-LTDH inal_rev1.pdf | http://celsiuscity.eu/wp-content/uploads/2019/11/Slough.pdf | https://www.iea-dhc.org/fileadmin/documents/Annex_X/IEA_Annex_X_Final_Report_2014_-_Toward_4th_Generation_District_Heating.pdf | https://backend.orbit.dtu.dk/ws/portalfiles/portal/142226895/Untitled.pdf
48 | ULTDH | ULTDH utilizing solar collectors for house heating | Drake Landing Solar Community, Okotoks, Alberta | Canada | 52 energy-efficient detached houses | Solar | 2,293 m² solar collectors located on garage roofs, heat is stored in central unit and then distributed in the community | Missing info | Solar collectors | No (water from DH is used to heat air which brings heat to consumer) | DHW is preprepared separately with solar collectors based on roofs and gas fired water heaters | Seasonal storage (boreholes) and short-term storage (Tank TES) | Centralised | 1.10.1.1.1. | Distribution investment cost: 151 €/m; Annual distribution cost 4.9 €/GJ |  |  | 39.6 | 40.2 |  |  | 31.9 |  |  | >700 kW solar collectors | 751.389 | 712.222 | 93.056 | 1.045 (trench) | 0.0295 | 0.26 | 5 | 0.024 | 694.444 | 0.565 (calculated from data-trench length) | http://celsiuscity.eu/wp-content/uploads/2019/11/Okotoks.pdf | https://www.iea-dhc.org/fileadmin/documents/Annex_X/IEA_Annex_X_Final_Report_2014_-_Toward_4th_Generation_District_Heating.pdf
49 | LTDH | LTDH utilizing existing DH for heating of passive houses | Hertings farm in Falkenberg | Sweden | Four multi-family passive houses | Existing DH/Solar | Existing DH (based on woodchips, pellets, bio oil, natural gas, fossil oil) that supplies HEX at consumer substation for SH and DHW (SH provided with air heating) | Missing info | MTDH network is connected directly to low energy buildings | No (water from DH is used to heat (preheated by solar energy) air which brings heat to consumer; also floor heating implemented) | No (network temperatures high enough) |  |  | N/A | Distribution investment cost: 206 €/m; Annual distribution cost 4.5 €/GJ |  |  | 73 | 85 |  |  | 43.5 |  |  | 0.712 | 381.667 | 348 | 34.167 | 0.342 (trench) | 0.014 | 0.73 | 9 | 0.025 | 1027.778 | 1.02 | https://www.iea-dhc.org/fileadmin/documents/Annex_X/IEA_Annex_X_Final_Report_2014_-_Toward_4th_Generation_District_Heating.pdf
50 | LTDH | LTDH utilizing existing DH for heating of passive houses | Söndrums Kyrkby in the city of Halmstad | Sweden | New construction multi-family and pair passive houses | Existing DH | Existing DH and electrical heaters for peak load supply consumer substation for SH and DHW (SH by heated air) | Missing info | MTDH network is connected directly to low energy buildings | No (water from DH is used to heat (preheated by solar energy) air which brings heat to consumer) | No (network temperatures high enough) |  |  | N/A | Distribution investment cost: 143 €/m; Annual distribution cost 6.6 €/GJ |  |  | 60 | 76 |  |  | 37 |  |  | 0.059 | 255.556 | 225 | 52.222 | 0.47 (trench) | 0.012 | 0.36 | 12 | 0.019 | 472.222 | 0.48 | https://www.iea-dhc.org/fileadmin/documents/Annex_X/IEA_Annex_X_Final_Report_2014_-_Toward_4th_Generation_District_Heating.pdf
51 | LTDH | LTDH utilizing solar heat and absorption HP for residential heating | Ackermannbogen – SNAB, Munich | Germany | 7 residential buildings | Solar/Existing DH | Solar collectors and absorption HP, existing DH as a back-up; Indirect od direct connection between SH and the main network | Missing info | Solar collectors; Shunt? (existing DH-Missing info) | No | IHEU | Tank TES (6000 m3) | Centralized | 3.2.1.1.1. | Distribution investment cost: 206 €/m; Annual distribution cost 3.2 €/GJ |  |  | 55 | 60 | 55 (direct connection) | 60 (direct connection) | 30 |  |  | 2.38 | 1815 | 1771.944 | 64.722 | 1.24 (trench) | 0.023 | 1.3 | 2 | 0.077 | 1416.667 | 1.43 | https://www.iea-dhc.org/fileadmin/documents/Annex_X/IEA_Annex_X_Final_Report_2014_-_Toward_4th_Generation_District_Heating.pdf
52 | LTDH | LTDH utilizing geothermal heat for residential heating | Kırşehir | Turkey | 1,800 standard dwellings in high-rise multi-family buildings (no need for renovation because heating system in buildings was oversized) | Geothermal | Geothermal power plant that produces heat sold in DH network; SH stops when there is need for DHW; Geothermal network is connected via HEX to distribution network; There is indication that there is direct connection between distribution network and consumer; Temperature of geothermal source is in range 56 to 57°C (return temperature 38°C); 2 oil boilers raise supply temperature of distribution network to 61°C during peak load | Missing info | HEX | No | IHEU |  |  | 1.13.2.1.1. | Investment: 1.8 mil €; Variable heat price: 59 ct/kWh | 57 | 19 |  | 54 |  | 53 | 41 (network); 40 (consumer substation) |  |  | 16.74 | [10 empty] | https://www.iea-dhc.org/fileadmin/documents/Annex_X/IEA_Annex_X_Final_Report_2014_-_Toward_4th_Generation_District_Heating.pdf
53 | NTDH | NTDH utilizing ground water for residential heating | March-Hugstetten | Germany | 55 low energy buildings | Ground water | Ground water runs through network feeding consumer substation HPs for SH and DHW | Missing info | Ground water runs through the network | HP | HP |  |  | 1.4.1.2.1. |  | 11 |  |  | 11 | [5 empty] | 0.76 |  |  |  | 2.5 | [5 empty] | 0.304 (calculated from data) | https://www.carmen-ev.de/biogene-festbrennstoffe/waermenetze/1966-waermenetze-neu-gedacht
54 | LTDH | LTDH utilizing solar panels, heating pump and existing DH for residential heating | Crailsheim | Germany | Multi-family buildings with 260 apartments, a school and gymnasium | Solar/Ground/Existing DH | Solar collectors (covering 50% of heating needs), ground HP and existing DH feeds DH network | Missing info | HP (ground); Solar collectors; Shunt? (existing DH-Missing info) | No | IHEU? (Missing info) | Borehole heat storage unit of 37500 m3, corresponding to a storage capacity of approximately 10000 m3 water; 2 water tanks (100 m3 and 480 m3) | Centralised | 1.3.2.1.1. | Investment: 8 mil. €; Variable heat price 19 ct/kWh |  |  |  | 65 |  |  | 35 |  |  | 5.1 | 3000 (solar collectors) | Solar collectors cover 50 % of heating needs | [8 empty] | https://www.carmen-ev.de/biogene-festbrennstoffe/waermenetze/1966-waermenetze-neu-gedacht | https://www.sciencedirect.com/book/9781782423744/advanced-district-heating-and-cooling-dhc-systems | https://www.solarthermalworld.org/installation/solar-district-heating-crailsheim-seasonal-borehole-storage | http://www.ubcwheel.eu/index.php/gpdp:gpdb/article/2450
55 | LTDH | LTDH utilizing geothermal power plant for industrial park heating | Győr | Hungary | Part of Győr District Heating System and Industrial Park | Geothermal | Geothermal power plant feeding the network | Missing info | Missing info | Missing info | Missing info |  |  | N/A | Investment: 5.94 mil. € | [9 empty] | 52 |  |  |  |  | 0.05 | [5 empty] | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/100-re-district-gyor-hungary/
56 | LTDH | LTDH utilizing geothermal power plant for existing DH network | Miskolc (Avas) | Hungary | Part of Avas District Heating System | Geothermal | Geothermal power plant feeding the network | Missing info | Missing info | Missing info | Missing info |  |  | N/A | Investment: 5.05 mil. € | [9 empty] | 55 |  |  |  |  | 0.05 | [5 empty] | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/100-re-district-miskolc-avas-hungary/
57 | LTDH | LTDH utilizing solar energy, ground HPs and CHP for residential heating | Alessandria | Italy | 800 apartment buildings | Solar/Ground/Gas | CHP, backup boilers, solar collectors and ground HP (to achieve high temperatures) feeding the network | Missing info | Missing info | Missing info | Missing info | Aquifer (2000 m3) | Centralized | N/A | [14 empty] | 60 | [6 empty] | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/100-re-district-alessandria-italy/
58 | ULTDH | ULTDH utilizing geothermal HP for heating of schools and residential buildings | Mieres (Barredo), Asturias | Spain | Polytechnic School of Mieres (EPM), the secondary school Bernaldo de Quirós (IBQ) and a group of buildings, located in the Vasco-Mayacina area, which has a total of 248 dwellings | Geothermal | 2 geothermal HsP used as a heat source that feeds DH network; Water from mine reservoirs through HEX feeds 2 HPs connected to network; Each house connected via HEX to main network; Back up gas boilers; 2 networks- 1 HTDH and other one LTDH 23 °C temperature of the source | Missing info | HP | No | Natural gas boilers |  |  | 1.13.1.1.1. | Investment: 1.42 mil. € | 23 |  |  |  | 45 |  |  | 5 |  | 2.63 | 2462.88 (supplied both to HTDH and LTDH |  |  |  | 1 | [5 empty] | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/100-re-district-mieres-barredo-asturias-spain/ | https://www.districtenergyaward.org/wp-content/uploads/2019/09/19GDECA-Desc-DHeating-BarredoColling-Spain.pdf
59 | LTDH | LTDH utilizing biomass power plant for village heating | Florina | Greece | 1.850 connected buildings of villages of Amyntaio, Levaia, Filotas | Biomass | Biomass power plant produces heat for DH network | Missing info | HEX? (Missing info) | Missing info | Missing info |  |  | N/A | Investment: 14.57 mil. € | [9 empty] | 30 |  |  |  |  | 0.058 | [5 empty] | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/100-re-district-florina-greece/
60 | NTDH | NTDH utilizing excess heat for heating of residential neighbourhood (renovated and nonrenovated houses) | Lund (Medicon Village) | Sweden | Newly built buildings, existing neighbourhood, mixed neighbourhood | Ground/Excess heat | Excess heat and ground heat network which is connected to consumer substation HPs used for SH and DHW; Excess heat from cooling | Yes | HEX (ground and excess heat) | HP | HP |  |  | 2.4.1.1.1. |  |  |  | 16 | 40 | [7 empty] | 10000 |  |  | 0.14 | [5 empty] | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/100-re-district-lund-medicon-village-sweden/ | http://ectogrid.com/use-cases/medicon-village/ | https://www.mediconvillage.se/sv/game-changing-technology-connects-medicon-village-buildings | https://www.mdpi.com/2071-1050/11/24/7051/htm
61 | LTDH | LTDH utilizing excess heat from research centers for other research facilities heating | Lund (Brunnshög) | Sweden | Research facilities of MAX IV and European Spallation Source, ESS and Science Village Scandinavia | Excess heat | Excess heat from cooling transfer heat via HEX to main network (before heat was transferred via HP to match 80 °C temperature mark of the network | Missing info | HEX (HP-before) | No | IHEU? (Missing info) |  |  | 2.4.2.1.1.* |  | 40 |  | 45 | 65 | 40 |  | 35 | [6 empty] | 4.5 | 1 | [5 empty] | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/lund-brunnshog/ | https://sciencevillage.com/en/projekt/low-temperature-district-heating-network/
62 | LTDH | LTDH utilizing excess heat for residential and office heating | Hoje-Taastrup (Østerby), Copenhagen | Denmark | Terraced houses with 158 dwellings, later on expansion to neighbouring areas with 350 houses, town hall and office buildings | Excess heat | Excess heat from cooling feeds the network, HP raises temperature of fluid used for SH and DHW | Missing info | HP | No | IHEU? (Missing info) | Aquifer (to be built) | Centralized | 2.4.2.2.1.* |  |  |  |  | 73 | 40 | 55 | 30 | 5.3 |  | 8.7 |  | 879 | 89 |  | 0.25 | 0.27 |  |  |  |  | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/hoje-taastrup-osterby-copenhagen-region-denmark-cool-dh-project/ | https://www.cooldh.eu/demo-sites-and-innovations-in-cool-dh/osterby-hoje-taastrup/ | https://heatpumpingtechnologies.org/annex47/wp-content/uploads/sites/54/2018/12/annex-47sub-projetcshje-taastrupdistrict-cooling.pdf | http://lup.lub.lu.se/luur/download?func=downloadFile&recordOId=8979223&fileOId=8979236
63 | LTDH | LTDH utilizing biogas for low energy houses heating | Windsbach (Neubaugebiet Badstraße) | Germany | 100 low energy houses | Biogas | Biogas CHP and boiler installed | Missing info | CHP | No | IHEU? (Missing info) | 2 buffer storage tanks (combined 40000 L) | Centralized | N/A | [7 empty] | 32.5 |  |  | 0,7 (CHP); 0,56 (boiler) |  | 1000 |  | 13 |  |  |  |  | 76.932 (calculated from data) |  | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/100-re-district-windsbach/ | https://portal.enerpipe.de/de/blog/226/neues-waermekonzept-fuer-neubaugebiete-
64 | LTDH | LTDH utilizing air and seawater for heating of a part of a town | Odense | Denmark | Whole area of Odense | Sea water/Air/Excess heat/CHP | HPs and CHP plant feed DH network | Missing info | Missing info | Missing info | Missing info |  |  | N/A | Investment: 267.61 mil. € | [20 empty] | https://www.euroheat.org/wp-content/uploads/2019/08/RHC-ETIP_District-and-DHC-Vision-2050.pdf | https://www.euroheat.org/knowledge-hub/case-studies/100-re-district-odense-denmark/
65 | LTDH | LTDH utilizing seawater/sewage for heating | Helsinki | Finland | Covers 4% of the network's total heat load | Sea water/Excess heat | Five 16.8 MW HPs connected to both heating and cooling network; In winter: heat is being recovered from sewer to preheat district heating return flow from 50 °C to 62 °C , the water goes to HP, sea water is used for cooling (free cooling); Summer: heat extracted from cooling network used to raise temperature of heating network (in summer 88 °C ), surplus heat is rejected to sea water; Source temperature from 10 °C (winter) to 22 °C (summer) | Yes | HP (sea water and sewer); DHN and DCN connected with HP | No | IHEU? (Missing info) | Aquifer | Centralized | 1.8.1.1.1. |  | 10 (winter-sewage); 22 (summer-seawater) |  | 62 (winter) | 88 (summer) |  |  | 45 (summer) to 50 (winter) | 2.96 (summer); 3.51 (winter) |  | 90.6 (summer); 83.9 (winter) | [10 empty] | https://www.gshp.org.uk/pdf/DECC_Heat_Pumps_in_District_Heating_Case_studies.pdf
66 | NTDH | NTDH utilizing ground heat pumps for residential and commercial heating | Wandsworth Riverside | England | 504 apartments, commercial and leisure space | Ground | 3 ground HPs feeding DH connected to substations for SH and DHW | Yes | HEX | HP | HP | Aquifer; Vertical ground HEX (8 boreholes 120 m depth) | Centralized | 1.7.1.2.2. |  | 15 | 8 |  |  | 45 |  | 35 (consumer substation) |  |  | 1.2 | [10 empty] | https://www.gshp.org.uk/pdf/DECC_Heat_Pumps_in_District_Heating_Case_studies.pdf
67 | LTDH | LTDH utilizing solar collectors and wood boilers for enclave heating | Büsingen | Germany | German enclave with residential buildings, school, hotel and public buildings | Solar/Biomass | 13% of heat supply comes from solar collectors and rest is supplied by two biomass boilers with outputs 900 kW and 450 kW (oil boilers as reserve) | Missing info | HEX? (biomass-Missing info); Solar collectors | Missing info | Missing info | Tank TES 100 m3 | Centralised | N/A | Investment: 3.5 mil. € |  |  |  | 80 |  | 80 | 50 |  |  | 0.9 and 0.45, (wood boilers); Solar collectors (Missing info) |  | 3500 |  | 6 |  |  |  |  | 583.333 (calculated from data) |  | https://www.carmen-ev.de/biogene-festbrennstoffe/waermenetze/1966-waermenetze-neu-gedacht
68 | LTDH | LTDH utilizing solar collectors and wood chip boiler for residential heating | Regensburg | Germany | 64 residential units in single-family, double and row houses | Solar/Biomass | Solar collectors cover around 20% of total annual heat required, wood chip boiler 450 kW | Missing info | HEX? (biomass-Missing info); Solar collectors | No? (Missing info) | IHEU? (Missing info) |  |  | N/A | Investment: 1.4 mil. € | [9 empty] | 0.45 (wood chip boiler); Solar collectors (Missing info) | 800 (wood chip boiler); Solar collectors (Missing info) | Solar collectors cover 20 % of heating needs | [8 empty] | https://www.carmen-ev.de/biogene-festbrennstoffe/waermenetze/1966-waermenetze-neu-gedacht
69 | LTDH | LTDH utilizing wood boiler for heating of various buildings | Grengiols | Switzerland | Multi-purpose facility, fire station and 3 households | Biomass | Boiler | Missing info | Missing info | Missing info | Missing info |  |  | N/A | [12 empty] | 160 | [8 empty] | https://www.enalpin.com/newsletter/files36/newsletter-nr.1-2016.pdf
70 | LTDH | LTDH utilizing thermal water heat pump for thermal resort heating | Burgerbad, Leukerbad | Switzerland | Thermal resort | Ground water | Thermal water HP for SH and DHW | Missing info | Missing info | Missing info | Missing info |  |  | N/A | [10 empty] | 1.2 |  | 4500 | [8 empty] | https://www.enalpin.com/newsletter/files36/newsletter-nr.1-2016.pdf
71 | NTDH | NTDH utilizing ground heat for heating of new Paris district | Paris Saclay | France | Scientific, engineering and business schools, research laboratories, private companies and housing area | Ground/Excess heat | Ground heats network connected to 8 HPs at consumer substations for SH and DHW | Yes | HEX (ground and excess heat) | HP | HP |  |  | 2.4.1.1.1. | Investment: 50 mil. € |  |  | 15 | 30 | 45 | 63 | 45 (consumer substation) |  |  | 37 | 40000 |  | 21 to 50 | 10 | 1.2 |  |  |  | At the end of the project, when network will cover heat demand of area of 1800 km2: 4300 kWh m(linear trench)/year | 3.7 (calculated from data) | https://www.euroheat.org/wp-content/uploads/2017/01/study-on-efficient-dhc-systems-in-the-eu-dec2016_final-public-report6.pdf
72 | LTDH | LTDH onnected to existing DH for passive house heating | Hyvinkää | Finland | Number of passive houses | Solar/Existing DH | Existing DH (wood pellet CHP plant and waste incineration plant) heats through HEX LTDH | Missing info | HEX | No | IHEU? (Missing info) |  |  | 3.2.1.1.1.* |  |  |  |  | 65 |  | 35 |  |  |  | 10 (CHP) |  | 1000.5 |  | 1.22 |  |  | 0.2 |  | 0.41 |  | https://doi.org/10.1016/j.egypro.2017.05.052 | https://backend.orbit.dtu.dk/ws/portalfiles/portal/142226895/Untitled.pdf
73 | LTDH | LTDH onnected to existing DH for passive house heating | Ludwigsburg-city quarter Sonnenberg | Germany | City quarter | Existing DH | Existing DH (CHP and ground HP-placed in one heating plant) | Missing info | Return line of main DH network | No | IHEU | Storages at every consumer are in planning phase | Decentralized | 3.1.2.3.1.* |  | 70 | 40 |  | 40 |  |  | 25 |  |  | 0.35 (gas CHP); 0.2 (ground HP)-main network | [10 empty] | https://doi.org/10.1016/j.egypro.2017.05.052 | https://backend.orbit.dtu.dk/ws/portalfiles/portal/142226895/Untitled.pdf
74 | LTDH | LTDH utilizing pellet boiler for heating of two buildings | Beļava | Latvia | 2 insulated buildings | Biomass | Central heating boiler (biomass) (first outline is for insulated houses 65°/35°C and second one for other buildings at 80°C/60°C) | Missing info | HEX? (Missing info) | No | IHEU? (Missing info) |  |  | 1.12.1.1.1. |  |  |  | 65 |  | 55 |  | 25 Consumer); 35 (network) |  |  | 0.199 | [10 empty] | http://www.lowtemp.eu/examples/first-season-with-low-temperature-district-heating-system-pilot-project-in-belava/
75 | NTDH | NTDH utilizing solar and ground energy as well as excess heat for heating of a part of a university | London South Bank University site in Southwark | England | University | Ground/Excess heat/Solar | Heat is transferred from ground into network (also solar collectors and excess heat); At the end of a network HPs for SH and DHW; Excess heat from cooling | Yes | HEX? (ground, and excess heat-Missing info); Solar collectors | HP | HP | Aquifer | Centralized | 2.4.1.1.2. | Investment: 4.7 mil. € | [5 empty] | 82 | [14 empty] | https://www.icax.co.uk/Balanced_Energy_Networks.html | https://www.gshp.org.uk/pdf/BEN_Balanced_Energy_Networks.pdf
76 | NTDH | NTDH utilizing air and ground heat for community heating | Easton, Bristol | England | 3 community buildings and 10 domestic homes | Ground/Air/Solar | Air and ground heating network connected to consumer booster HPs for SH and DHW* | Yes (air) | HEX (ground); Solar collectors; Air (HP) | HP | HP | Vertical ground HEX (boreholes) | Centralised | 1.2.1.1.1. |  | 25 | [10 empty] | 280 | [8 empty] | https://www.icax.co.uk/Owen_Square_Community_Energy_Project.html
77 | ULTDH | ULTDH utilizing solar heat for house heating | Geding | Denmark | 25 houses | Solar | Currently still operating boiler (for LTDH but in the future it will be replaced with solar collectors and HPs at consumer substations for SH and DHW | Missing info | Solar collectors | No | HP | Storage is in planning phase | Centralized | 1.10.1.1.2. |  |  |  | 30 | 45 | [16 empty] | https://www.sweco.dk/en/our-offer/cases/energy/converting-district-heating-from-conventional-to-ultra-low-temperature-district-heating/
78 | LTDH | LTDH utilizing return water in existing DH for residential heating | Berlin-Adlershof | Germany | Residential area „Living at the Campus“ | Existing DH | Existing DH return flow feeds LTDH network; Solar field will be connected to network | Missing info | Return line of main DH network | No | IHEU? (Missing info) |  |  | 3.1.2.3.1.* |  |  |  | 60 | 65 | [10 empty] | 0.19 | [5 empty] | https://www.imp.gda.pl/ee_cities/prezentacje/drugi_C/1_Britta_Schmigotzki.pdf | http://www.lowtemp.eu/uncategorized/living-on-campus-berlin-adlershof-btbs-LTDH ystem-with-solar-feed-in/ | https://www.adlershof.de/en/news/district-heating-with-sun-power-1/
79 | LTDH | LTDH onnected to existing DH for residential heating | Växjö | Sweden | Apartment buildings | Existing DH | Connected to existing DH, mixing supply and return water in shunt to achieve desired temperatures | Missing info | Shunt | No | IHEU? (Missing info) |  |  | 3.1.2.1.1.* |  |  |  | 65 | [17 empty] | http://www.smartcity-ready.eu/low-temp-dh-being-installed-in-vaxjo/
80 | LTDH | LTDH utilizing excess heat for residential heating | Wörgl | Austria | 20 low energy houses | Excess heat/Biomass | Biomass plant and 3 heat pumps utilizing excess heat at local dairy plant for DH | Missing info | HP (excess heat) | No | IHEU? (Missing info) |  |  | 1.12.1.1.1. | [14 empty] | 0.16 | [6 empty] | https://thermaflex.com/gb/case-studies/high-speed-sustainable-heating-network-in-worgl | https://www.pbpsa.com/articles/content/wrgl-district-energy-at | https://thermaflex.com/en/download/preview/670
81 | NTDH | NTDH utilizing heat from sea water for heating | Ulstein | Norway | Town | Sea water | Sea water transfer heat to network; Booster HPs at consumer substation for SH and DHW | Yes | HEX? (Missing info) | HP | HP |  |  | 1.7.1.1.1.* |  | 6.5 | [10 empty] | 20000 | [8 empty] | https://backend.orbit.dtu.dk/ws/files/142226895/Untitled.pdf
82 | LTDH | LTDH utilizing excess heat for town heating | Middelfart | Denmark | City of Middelfart, 5000 consumers | Excess heat | Excess heat from industry, reserve capacity that utilizes natural gas or fuel oil | Missing info | HEX? (Missing info) | No | IHEU? (Missing info) |  |  | 2.1.2.1.1.* |  |  |  | 65 | 67 |  |  | 40 |  |  |  | 122086 (94491 from excess heat and the rest from gas boilers) | 103462.712 (calculated from data) |  | 148 |  |  | 18 |  | 699.072 (calculated from data) |  | https://backend.orbit.dtu.dk/ws/portalfiles/portal/142226895/Untitled.pdf | https://www.upgrade-dh.eu/hr/middelfart-danska/
83 | LTDH | LTDH utilizing ground heat for apartment heating | Stockholm Husby | Sweden | 5 apartment buildings (430 apartments) | Ground | Utilization of HP* | Missing info | HP? (Missing info) | No? (Missing info) | IHEU? (Missing info) | 2 vertical ground HEXs (total 98 boreholes) | Centralized | 1.1.2.1.1.* | [15 empty] | 0.023 | [5 empty] | http://www.oppenfjarrvarme.se/media/Heat-Recovery-from-Data-Centers-Guided-Tour-20150121.pdf
84 | LTDH | LTDH utilizing geothermal heat pump for warming up a soccer field | Katrineholm Backavallen | Sweden | Soccer Field | Ground/Excess heat | Excess heat from ice compressors and heat from ground used for HPs for SH and DHW | Missing info | HP? (ground-Missing info); HEX? (excess heat-Missing info) | No? (Missing info) | IHEU? (Missing info) |  | Centralized | 2.1.2.1.1.* | [21 empty] | http://etkhpcorderapi.extweb.sp.se/api/file/1946
85 | LTDH | LTDH utilizing ground heat pump for residential heating, hotel and free cooling in office buildings | Gothemburg - Molndal | Sweden | Low energy apartment buildings, office building, and hotel building. | Excess heat | Excess heat from high temperature heating of historical industrial building/office heated from DH, is used to heat residential buildings then storing in 130 boreholes and HPs for DHW | Missing info | HEX? (Missing info) | No? (Missing info) | HP | Vertical ground HEX (130 boreholes) | Centralised | 2.5.2.1.1.* | [21 empty] | https://grist.files.wordpress.com/2010/09/gothenburg,_sweden_i-district_energy_climate_award.pdf | https://www.euroheat.org/wp-content/uploads/2017/09/1.2-171024_1400-1530-2-POL-Jonas-Cognell-Goteborg-Energi.pdf
86 | LTDH | LTDH onnected to existing DH for residential heating | Robinielunden, Albertslund | Denmark | 48 dwellings, non-profit social housing | Existing DH | The LTDH s produced by mixing hot DH water with colder return water from remaining DH areas. The DH comes mainly from waste incineration, and from CHP on biomass | Missing info | Shunt? (Missing info) | No? (Missing info) | IHEU? (Missing info) |  |  | 3.1.2.1.1.*
87 | LTDH | LTDH onnected to existing DH for residential heating | Askebo, Albertslund | Denmark | 41 dwellings, private attached houses | Existing DH | The LTDH s produced by mixing hot DH water with colder return water from remaining DH areas. The DH comes mainly from waste incineration, and from CHP on biomass | Missing info | Shunt? (Missing info) | No? (Missing info) | IHEU? (Missing info) |  |  | 3.1.2.1.1.*
88 | LTDH | LTDH onnected to existing DH for residential heating | Alberts Have, Albertslund | Denmark | 72 dwellings, non-profit social housing | Existing DH | The LTDH s produced by mixing hot DH water with colder return water from remaining DH areas. The DH comes mainly from waste incineration, and from CHP on biomass | Missing info | Shunt? (Missing info) | No? (Missing info) | IHEU? (Missing info) |  |  | 3.1.2.1.1.*
89 | LTDH | LTDH onnected to existing DH for residential heating | Albertslund West, Albertslund | Denmark | 456 dwellings (refurbishment is not completed) | Existing DH | The LTDH s produced by mixing hot DH water with colder return water from remaining DH areas. The DH comes mainly from waste incineration, and from CHP on biomass | Missing info | Shunt? (Missing info) | No? (Missing info) | IHEU? (Missing info) |  |  | 3.1.2.1.1.*
90 | NTDH | NTDH utilizing ground for residential heating | Heidegarten area in Rieseby | Germany | About 47 residential units | Ground | Ground heat network that is connected to consumer substation HPs for SH and DHW* | Missing info | HEX? (Missing info) | HP | HP |  |  | 1.1.1.1.1.* |  |  |  | 0 | 20 |  |  |  | 4.5 | [12 empty] | https://www.schleswiger-stadtwerke.de/content/produkte/schleswigerNAHWAERME/technik_schleswiger_nahwaerme.php
91 | NTDH | NTDH utilizing ground heat pumps for residential heating | Bregning-West area in Husby | Germany | About 19 residential units | Ground | Ground heat network that is connected to consumer substation HPs for SH and DHW* | Missing info | HEX? (Missing info) | HP | HP |  |  | 1.1.1.1.1.* |  |  |  | 0 | 20 |  |  |  | 4.5 | [12 empty] | https://www.schleswiger-stadtwerke.de/content/produkte/schleswigerNAHWAERME/technik_schleswiger_nahwaerme.php
92 | NTDH | NTDH utilizing ground and solar collectors for residential heating | Alte Fachhochschule area in Eckernförde | Germany | About 93 residential units | Ground/Solar | Solar collectors in network; HPs in buildings for SH and DHW | Missing info | HEX? (ground-Missing info); Solar collectors | HP | HP |  |  | 1.2.1.1.1.* |  |  |  | 0 | 20 |  |  |  | 4.5 | [12 empty] | https://www.schleswiger-stadtwerke.de/content/produkte/schleswigerNAHWAERME/technik_schleswiger_nahwaerme.php
93 | NTDH | NTDH utilizing CHP plant and air HP for residential heating | Wanderup | Germany | About 40 residential units | Air/Gas | CHP and HPs at consumer substation for SH and DHW | Missing info | HP? (air-Missing info) | HP? (Missing info) | HP? (Missing info) |  |  | 1.9.1.1.1.* |  |  |  | 45 | 45 | [16 empty] | https://www.schleswiger-stadtwerke.de/content/produkte/schleswigerNAHWAERME/technik_schleswiger_nahwaerme.php
94 | NTDH | NTDH utilizing ground for residential heating | Geltinger Bucht area in Gelting | Germany | About 121 residential units | Ground | Ground heats network that is connected to consumer substation HPs for SH and DHW* | Missing info | HEX? (Missing info) | HP? (Missing info) | HP? (Missing info) |  |  | 1.1.1.1.1.* | Heat price 7 ct/kWh |  |  | 0 | 20 |  |  |  | 4.5 | [5 empty] | 10 | [6 empty] | https://www.schleswiger-stadtwerke.de/content/produkte/schleswigerNAHWAERME/geltinger_bucht.php | https://www.schleswiger-stadtwerke.de/downloads/glasfaser_nahwaerme/PreisbersichtKalteNahwrme-GeltingerBucht.pdf?m=1502781058
95 | NTDH | NTDH utilizing pellet boiler and ground for residential heating | Geltinger Birk area in Gelting | Germany | About 49 residential units | Ground/Biomass | HPs in every building (pellets use optional) for SH and DHW | Missing info | HEX? (ground and pellets-Missing info) | HP | HP |  |  | 1.3.1.1.1.* |  |  |  | 0 | 20 |  |  |  | 4.5 | [12 empty] | https://www.ostsee-reetdorf.de/oekologie/
96 | NTDH | NTDH utilizing sea water for district heating | Eco district ALLAR (Massileo) - Marseille | France | District | Sea water/Excess heat | Sea water heats network through HE; At consumer substation HPs for SH and DHW; Excess heat from cooling for network | Yes | HEX? (sea water and excess heat-Missing info) | HP | HP |  |  | 2.4.1.1.1.* |  |  |  | 12 | 24 | 35 | 40 |  |  |  | 22 |  |  |  |  | 0.027 | [5 empty] | https://www.dalkia.fr/en/media/press-releases/optimal-solutions-unveils-massileoc-marseilles-new-smart-renewable-energy | https://www.massileo.fr/sites/massileo/files/2019-03/Plaquette%20Massileo_0.pdf | https://www.massileo.fr/node/136
97 | NTDH | NTDH utilizing excess heat from sewage for stadium and shopping centre heating | Eco district Vélodrome - Marseille | France | Stadium, shopping centre | Excess heat | DH utilizing excess heat; HPs at consumer substation for SH and DHW* | Missing info | HEX? (Missing info) | HP? (Missing info) | HP? (Missing info) |  |  | 2.5.1.1.1.* | [21 empty] | http://www.afpg.asso.fr/wp-content/uploads/2019/08/APFG_GUIDE_BoucleEau_05082019.pdf
98 | NTDH | NTDH utilizing excess heat from sewage for multipurpose district heating | Eco district "CAP AZUR" - Roquebrune-Cap-Martin | France | Eco-neighbourhood (300 offices, shops and homes)-7 buildings | Excess heat | Heat recovery (exchangers) from nearby water treatment plant, HPs at each building to increase or decrease water temperature | Yes | HEX | HP | HP |  |  | 2.3.1.1.1. |  | 20 | 2 | 15 | 25 |  | 45 | 40 (consumer substation); 18 (network) | [7 empty] | 0.07 | [5 empty] | http://www.afpg.asso.fr/wp-content/uploads/2019/08/APFG_GUIDE_BoucleEau_05082019.pdf | https://www.edf.fr/sites/default/files/contrib/collectivite/transition-energetique/pages-references/fiche_presse_roquebrune.pdf | https://www.dalkiasmartbuilding.fr/ecoquartier-cap-azur-reseau-deau-temperee | https://www.edf.fr/sites/default/files/contrib/groupe-edf/premier-electricien-mondial/cop21/solutions/pdf/cop21-solutions_roquebrune_va.pdf
99 | NTDH | NTDH utilizing ground for multipurpose district heating | Eco district of " Fort – Issy-les-Moulineaux" - Paris | France | District (1.538 housing units, 1.600 m2 of shops, public and leisure buildings | Ground | HPs located in buildings receive water from loop (geothermal source) for SH and DHW | Yes | HEX? (Missing info) | HP | HP |  |  | 1.1.1.1.1.* |  |  |  |  | 28 | [10 empty] | 0.12 | [5 empty] | http://reseaux-chaleur.cerema.fr/reseau-de-geothermie-de-lecoquartier-du-fort-issy-les-moulineaux-hauts-de-seine | http://www.afpg.asso.fr/wp-content/uploads/2019/08/APFG_GUIDE_BoucleEau_05082019.pdf
100 | NTDH | NTDH utilizing geothermal energy for district heating | Jonzac | France | District | Ground | Ground heats network; HPs at consumer substation for SH and DHW | Yes | HEX | HP | HP |  |  | 1.1.1.1.1. | [21 empty] | https://www.dalkia.fr/fr/e-mag-efficacite-energetique/optimal-solutions-obtient-le-premier-titre-v-reseau-deau-temperee | http://geoatlantic.eu/portfolio/wp-content/uploads/2019/05/SLIDE-PRESENT-GEOTH-JONZAC.pdf | http://www.afpg.asso.fr/wp-content/uploads/2019/08/APFG_GUIDE_BoucleEau_05082019.pdf
101 | NTDH | NTDH utilizing ground water for multipurpose district heating | Ile Folien in Valenciennes | France | District with houses, offices and shops | Ground water | HPs at consumer substations for SH and DHW | Missing info | Central HP utilizes ground water?/Water through HEX exchanges heat with network?/Ground water runs through the network? (Missing info) | HP | HP |  |  | 1.4.1.1.1.* | Investment: 2.8 mil. € |  |  |  |  | 40 | 45 |  |  |  |  | 811 |  |  | 2.6 | 0.052 | [5 empty] | http://www.afpg.asso.fr/wp-content/uploads/2019/08/APFG_GUIDE_BoucleEau_05082019.pdf | http://www.cerdd.org/Parcours-thematiques/Changement-climatique/Initiatives-changement-climatique/Geothermie-innovante-pour-un-reseau-d-eau-a-Valenciennes
102 | NTDH | NTDH utilizing sea water for residential heating | La Seyne sur mer | France | 980 homes | Sea water | Sea water transfer heat through HEX; Network connected to booster HPs for SH and DHW | Yes | HEX | HP | HP |  |  | 1.7.1.1.1. | Investment: 1.7 mil. € | 12 | 15 | 12 | 15 | [9 empty] | 0.5 | [6 empty] | http://www.var-entreprises.com/thalassothermie-seyne-acte-ii/
103 | NTDH | NTDH utilizing ground for commercial heating | AIRBUS headquarter in Blagnac | France | 2 office buildings and one business-to-business restaurant building | Ground | Ground transfer heat to network; HPs at consumer substation for SH and DHW | Yes | HEX? (Missing info) | HP | HP | Vertical ground HEX (141 boreholes 205 m depth) | Centralized | 1.1.1.1.1.* |  |  |  |  | 35 |  |  | 30 | 6.5 to 6.8 | 5 to 5.9 | 2 |  |  |  | 0.2 | 0.05 |  |  |  |  | 10 (calculated from data) | http://www.afpg.asso.fr/wp-content/uploads/2019/08/APFG_GUIDE_BoucleEau_05082019.pdf | https://www.actu-environnement.com/ae/news/airbus-geothermie-siege-social-boucle-eau-temperee-33807.php4
104 | NTDH | NTDH utilizing excess heat from sewage for district heating | Bassins á flots - Bordeaux | France | District | Excess heat | Excess heat source of heat for network; HPs for SH and DHW | Missing info | HEX? (Missing info) | HP? (Missing info) | HP? (Missing info) |  |  | 2.5.1.1.1.* | [21 empty] | http://www.afpg.asso.fr/wp-content/uploads/2019/08/APFG_GUIDE_BoucleEau_05082019.pdf
105 | NTDH | NTDH utilizing excess heat from sewage for town hall and neighbourhood heating | Schallstadt Weiermatten | Germany | The new town hall and the 'Sonnengrün' block | Excess heat | Excess heat from waste water; HPs for SH and DHW* | Missing info | HEX? (Missing info) | HP? (Missing info) | HP? (Missing info) |  |  | 2.3.1.1.1.* |  |  |  | 12 | 17 | [9 empty] | 0.7 | [6 empty] | https://www.energiedienst.de/presse-detail/news/1288-heiss-auf-waermequelle-aus-dem-untergrund-im-baugebiet-weiermatten-abwasser-fuer-heizung-nutzte/
106 | NTDH | NTDH utilizing heat from solar thermal, ground and biomass for multipurpose community heating | Bodenmais | Germany | Bakery, petrol station, pizzeria and 12 houses | Ground/Solar/Biomass | Solar collectors produce heat as well as ground; that heat is transferred to consumer substation HPs for SH and DHW; Biomass boiler as back-up | Missing info | HEX? (ground and biomass-Missing info); Solar collectors | HP | HP | Ground buffer storage (25000 l)/500 l tank TES | Centralised/Decentralised | 1.3.1.1.1.* | [5 empty] | 20 | 80 (biomass boiler) | [8 empty] | 0.05 | [5 empty] | https://www.waermepumpe.de/uploads/tx_bcpageflip/Broschuere_Siedlungen_Novelle_2018_web.pdf
107 | NTDH | NTDH utilizing ground for residential heating | Grüne Höfe, Esslingen | Germany | 3 buildings (47 apartments) | Ground | Network receives heat from ground; Booster HPs connected to network for SH and DHW | Missing info | HEX? (Missing info) | HP | HP | Vertical ground HEX (29 boreholes 111 m depth) | Centralized | 1.1.1.1.1.* | [10 empty] | 0.2 | [10 empty] | https://www.kibele-bauumwelt.de/tl_files/content/Referenzen/PROJEKT_Gruene%20Hoefe_ES.pdf
108 | NTDH | NTDH utilizing ground water for residential heating | Afrastraße, Friedberg | Germany | 250 residential units | Ground water | Ground water heats brine water through heat exchanger; Then brine water is used in consumer substation HPs for SH and DHW | Missing info | HEX | HP | HP |  |  | 1.4.1.1.1. |  |  |  | 10 | [11 empty] | 0.03 | [5 empty] | https://www.pressebox.de/inaktiv/lechwerke-ag/Kalte-Nahwaerme-in-der-Praxis-Lechwerke-und-Stadtwerke-Friedberg-setzen-innovatives-Energiekonzept-um-zentrale-Gewinnung-von-Umweltwaerme-dezentrale-Erzeugung-von-Heizwaerme-in-den-Gebaeuden-durch-Waermepumpen/boxid/932640
109 | NTDH | NTDH utilizing excess heat from sewage for residential heating | Biebricher Schlosspark, Wiesbaden | Germany | 80 residential units | Excess heat | Sewage excess heat and excess heat from waste water; HEX is used to transfer heat to network; at each substation HPs for SH and DHW | Yes | HEX | HP | HP |  |  | 2.3.1.1.1. | Investment: 0.8 mil. € |  |  | 10 | 20 | [6 empty] | 523 | [9 empty] | https://www.wiesbadener-kurier.de/lokales/wiesbaden/nachrichten-wiesbaden/neue-technik-soll-geplante-hauser-am-biebricher-schlosspark-beheizen_18449052
110 | LTDH | LTDH utilizing GSHP, ASHP, excess heat and biomass for district heating | Eco-district Nanterre Coeur University | France | District | Ground/Air/Biomass/Excess heat | HPs used for network heating as well as CHP and excess heat | Missing info | HP (ground; air-Missing info); HEX? (biomass and excess heat-Missing info) | No | IHEU? (Missing info) | Vertical ground HEX (90 boreholes 150 m depth) | Centralized | 1.3.2.1.1.* | [21 empty] | https://www.dalkiasmartbuilding.fr/double-smart-grid-ecoquartier-nanterre-coeur-universite | http://www.ccibusiness-grandparis.fr/actualite/134726-un-double-smart-grid-pour-nanterre-coeur-d-universite
111 | LTDH | LTDH utilizing GSHP for hotel and park heating | Gardanne | France | Hotel, activity park and the Cité des Sciences de la Métropole Aix Provence Marseille | Ground | HPs used ground for SH and DHW | Missing info | HP | No | IHEU? (Missing info) |  |  | 1.1.2.1.1.* | [15 empty] | 0.14 | [5 empty] | https://www.dalkia.fr/fr/e-mag-efficacite-energetique/gardanne-un-nouveau-reseau-energies-renouvelables
112 | LTDH | LTDH utilizing existing DH return flow for building heating | Nottingham | England | 94 buildings | Existing DH | Existing medium temperature DH (return flow) for LTDH | Missing info | Return line of main DH network | No | IHEU? (Missing info) |  |  | 3.1.2.1.1.* |  |  |  | 50 | 60 |  |  | 30 | [13 empty] | https://www.bable-smartcities.eu/explore/use-cases/use-case/?L=0&tx_ndusecase_pi3%5BuseCase%5D=256&tx_ndusecase_pi3%5Baction%5D=show&tx_ndusecase_pi3%5Bcontroller%5D=UseCase&cHash=adcbf7b7196993f06b63edee4ef2fbfb
113 | LTDH | LTDH utilizing existing DH and solar collectors for district heating | Brühl district in Chemnitz | Germany | 1300 residential units and commercial units | Solar/Existing DH | Solar collectors and return flow of existing DH (lignite CHP plant) used as source for LTDH | Yes | HEX (existing DH); Solar collectors | No | IHEU | Two-zone storage (1000 m3+500 m3) | Centralized | 3.2.1.1.1.* |  |  |  |  | 70 |  |  | 57.5 | [7 empty] | 0.01 | [5 empty] | http://proceedings.ises.org/paper/swc2017/swc2017-0032-LalShrestha.pdf
114 | NTDH | NTDH utilizing excess heat for residential heating | Marktgemeinde Meitingen | Germany | Multi-dwelling building (20 dwelling units)-it will expand | Excess heat | Excess heat heating network; HPs for SH and DHW; Excess heat from cooling in industry | Missing info | HEX? (Missing info) | HP | HP | TES in every building | Decentralized | 2.1.2.1.1.* |  |  |  |  | 31 | [16 empty] | https://www.bifa.de/en/news/detail-view/news/low-temperature-district-heating-network-in-meitingen
115 | LTDH | LTDH utilizing excess heat for residential heating | Delft | Netherlands | 1600 homes | Excess heat/CHP | Excess heat (from sewage treatment plant) to heat network; HPs raises temperature of a water (back-up and peak demand covered by gas boilers) | Missing info | HP (excess heat) | No | IHEU? (Missing info) |  |  | 2.3.2.1.1.* |  |  |  | 40 | 70 | [5 empty] | 24 (CHP) | [10 empty] | https://energy-cities.eu/best-practice/hot-news-a-local-district-heating-company-established/
116 | NTDH | NTDH utilizing ground for residential heating | Am Vohbach, Burgheim | Germany | 40 housing units | Ground | Ground heats network; Network connected to consumer substation HPs for SH and DHW* | Missing info | HEX? (Missing info) | HP | HP | Vertical ground HEX (60 boreholes up to 70 m depth) | Centralized | 1.1.1.1.1. | Investment: 1 mil. € | [20 empty] | http://www.eb-ei.de/wp-content/uploads/2018/05/BEG-6.-Generalversammlung-16.05.2018-Final.pdf | https://www.burgheim.de/Leben-in-Burgheim/Bauen-Wohnen/Bauplaetze.htm/Seiten/Kaltes-Nahwaermenetz-KNWN.html? | https://www.donaukurier.de/lokales/neuburg/Burgheim-Ein-kaltes-Netz-fuer-ein-warmes-Burgheim;art1763,3567389
117 | NTDH | NTDH utilizing ground water for community heating | Dollnstein | Germany | 300 person community (2 commercial units, 7 municipal units, 31 residential units) | Ground water/Solar/Gas | Ground water HP and solar collectors heat fluid that is stored in storages; Gas CHP additionally raises temperature of fluid for SH and DHW; Gas boiler used as back-up | Missing info | HP (ground water); Solar collectors | HP | HP | Buffer tank 27000 l (80 °C); Low temperature tank 15000 l (25 °C) | Centralized | 1.4.1.1.1. | Investment: 1.3 mil. €; Price: 11 ct/kWh |  |  | 25 |  |  | 80? |  |  |  | 0.44 (water HP); 0.25 (CHP); 0.3 (gas boiler) |  | 100000 |  | 1.8 | [6 empty] | https://www.waermepumpe.de/uploads/tx_bcpageflip/Broschuere_Siedlungen_Novelle_2018_web.pdf | https://blog.paradigma.de/kaltes-netz-energie-dollnstein/
118 | ULTDH | ULTDH utilizing ground and solar heat for housing estate heating | Kassel | Germany | Housing estate (127 houses) | Ground/Solar | Central HP connected to ground feeds DH with heat; Solar collectors used to recover ground and for DHW preparation | Missing info | HP (ground) | No | Solar collectors | Vertical ground HEX (boreholes) | Centralized | 1.11.2.1.1. | Investment: 3.7 mil. € |  |  | 40 | [9 empty] | 45 | [7 empty] | https://backend.orbit.dtu.dk/ws/portalfiles/portal/142226895/Untitled.pdf
119 | NTDH | NTDH utilizing ground as heat source for community heating | Bad Nauheim Süd | Germany | Community | Ground | Ground heats brine water mixture; HE heats network fluid; Network connected to booster HPs for SH and DHW (consumer substation) | Missing info | HEX | HP | HP |  |  | 1.1.1.1.1. |  | 10 |  | 0 | 20 | [16 empty] | https://ecoconcepts.eu/wp-content/uploads/2018/07/Kalte_Nahwaerme_Netze_WTK_SWBadNauheim_D_130618_online.pdf
120 | NTDH | NTDH utilizing ground, solar and CHP as heat source for district heating | Frankfurt am Main | Germany | District | Ground/Solar | Decentralized HP, solar collectors and CHP connected to the network, every substation has HPs | Missing info | HP (ground); Solar collectors; CHP | HP | HP | Vertical ground HEX | Centralized | 1.2.1.2.1. |  | 13.5 |  |  | 35 | [5 empty] | 1.45 | [10 empty] | https://www.waermepumpe.de/fileadmin/user_upload/bwp_service/Forum_Waermepumpe/Praesentationen/Vortrag_Stawiarski_Waermetagung_klein.pdf
121 | NTDH | NTDH utilizing solar energy and excess heat from community heating | Berlin-Lichterfelde | Germany | 18 multi-family buildings (841 apartments) | Ground/Excess heat/Solar | Solar collectors and excess heat connected to the network (consumer substations equipped with HP for SH and DHW | Missing info | HEX? (ground-Missing info); Solar collectors | HP | HP | Vertical ground HEX? (temperatures 3 to 23 °C) | Centralized | 1.3.1.1.1. |  | 13 (ground) | [19 empty] | https://www.waermepumpe.de/fileadmin/user_upload/bwp_service/Forum_Waermepumpe/Praesentationen/Vortrag_Stawiarski_Waermetagung_klein.pdf